Implementasi 3-Bus Hybrid PV–Battery–Inverter

Dokument ini berisi empat deliverable yang Anda minta untuk skripsi: (A) diagram blok EMS untuk Simulink, (B) flowchart algoritma kontrol hybrid microgrid, (C) SLD final versi hybrid (penjelasan dan mapping ke model Simulink), dan (D) bab skripsi tentang arsitektur kontrol. Gambar SLD referensi yang Anda kirim: /mnt/data/sld.png.

A. Diagram Blok EMS untuk Simulink (Supervisory Controller)

Deskripsi singkat: EMS adalah blok supervisory yang menerima masukan dari metering, inverter, generator, dan BMS. EMS mengeluarkan setpoint ke inverter (P/Q refs + mode), bidirectional converter (I_ref atau P_ref), MPPT enable/disable, dan relay/breaker control untuk load shedding / islanding.

I/O utama EMS (Simulink Subsystem):

- Inputs:

  - P_load_bus[i] (kW) — per-bus (i = 1..3)

  - Q_load_bus[i] (kVAR) — per-bus

  - P_gen[i], Q_gen[i], V_bus[i], f_bus[i] — dari generator measurement

  - P_pv[i], Vdc_pv[i], I_pv[i] — dari PV/MPPT

  - SoC_batt[i], I_batt[i], V_batt[i], Temp_batt[i] — dari BMS

  - Grid_status (boolean), TOU_price(t) (Rp/kWh atau $/kWh)

  - Priority_loads[i][j] — daftar prioritas beban

- Outputs:

  - P_ref_inv[i], Q_ref_inv[i] (setpoint untuk inverter)

  - Mode_inv[i] (GRID_FOLLOW / GRID_FORM / IDLE)

  - Charge_enable[i] / Discharge_enable[i] (to bidirectional conv.)

  - I_ref_batt[i] (current reference ke bidir converter)

  - MPPT_enable[i] (on/off jika diperlukan)

  - Breaker_cmd[i] (open/close untuk islanding)

  - Load_shed_cmd[i][j] (boolean)

  - Logging & Events (ke file/log subsystem)

Sub-blocks internal EMS:

- Data acquisition & filtering — anti-aliasing, moving average untuk P/I measurement.

- State Estimation — hitung SoC_est, prediksi PV (simple persistence or irradiance input), load forecast (last-day pattern or simple moving average).

- Policy Engine (Rule-based) — menentukan tindakan cepat berdasarkan kondisi (grid up/down, SoC thresholds, TOU price).

- Optimizer (optional) — MPC or linear program module untuk optimisasi ekonomi (energy + battery lifetime) pada horizon T.

- Mode Manager — menentukan mode operasi per bus + master selection untuk islanding.

- Protection & Interlocks — semua keputusan diverifikasi terhadap proteksi (SoC limits, overcurrent, thermal). Jika violation, safety-first (disconnect battery/inverter).

- Communication bus — output ke data logger / UI.

Diagram blok (ASCII) — untuk dimasukkan di Simulink sebagai subsystem hierarchy:

+-------------------------------------------------------------+

| EMS_Controller (Subsystem)                                  |

|  +------------------+   +------------------+   +----------+ |

|  | Data Acquisition |-->| State Estimation |-->| Policy   | |

|  +------------------+   +------------------+   | Engine   | |

|                                                   +--------+ |

|  +-----------------+   +---------------+   +---------------+ |

|  | Optimizer (MPC) |   | Mode Manager  |   | Protection   | |

|  +-----------------+   +---------------+   +---------------+ |

|                         | Outputs (setpoints, breakers, logs) | |

+-------------------------------------------------------------+

Catatan implementasi Simulink:

- Buat satu Subsystem bernama EMS_Controller.

- Gunakan MATLAB Function block untuk Policy Engine (pseudocode bisa langsung dipaste — tersedia di bagian D).

- Jika ingin MPC, gunakan Model Predictive Control Toolbox atau buat custom QP solver di Simulink.

- Simulasi komunikasi: hubungkan signals secara langsung antar subsystem; untuk real-time hardware, gunakan Modbus/CAN blocks.

B. Flowchart Algoritma Kontrol Hybrid Microgrid

Tujuan flowchart: menggambarkan keputusan high-level EMS pada waktu nyata.

Flowchart (linier, dituliskan sebagai urutan langkah dengan kondisi):

- Start / Initialization

  - baca parameter awal (SoC_init, export_limit, TOU calendar, priority loads)

  - set defaults: Mode = GRID_CONNECTED if grid present

- Loop utama (periode T_loop, mis: 1s atau 100ms)

  - baca sensor: P_pv, P_load, SoC, Grid_status, Vbus, fbus, TOU_price

  - pre-process (filter) data

- Grid presence check

  - if Grid_status == false → goto ISLANDING_PROCESS

  - else continue

- Normal grid-connected routine
a. Local supply prioritization:

  - if P_pv >= P_load:

    - supply load from PV

    - if SoC < SoC_max_charge and MPPT_excess > Charge_min → charge battery

    - else if export_allowed & TOU_price_high → export excess to grid (set P_ref_inv accordingly)

  - else (PV insufficient):

    - if SoC > SoC_discharge_min → discharge battery to meet deficit (peak shaving logic)

    - else import from grid
b. Peak shaving decision: use short-window moving average of load; if predicted peak > threshold → pre-discharge
c. Economic decision (TOU): if TOU_price_high and SoC above threshold → discharge to reduce grid draw or export

- ISLANDING_PROCESS (Grid down)

  - Select master inverter (highest SoC or pre-configured)

  - Command master to GRID_FORMING (set Vref, fref)

  - Others GRID_FOLLOW but may go to GRID_FORM for sharing via droop

  - Check total available generation (PV + batt + synchronous gens)

  - If sum_generation >= critical_load → supply critical loads

  - Else perform load shedding according to priority list until balance achieved

- Protection checks (every loop)

  - if overcurrent on inverter or battery → reduce setpoints or disconnect

  - if SoC < minimum → force load shedding / prevent further discharge

  - if thermal alarms → isolate component

- Logging & Telemetry

  - send events to logger, update HMI

- Wait T_loop then repeat

Pseudocode ringkas (MATLAB function style) tersedia di bab D.

C. SLD Final (Hybrid) — Penjelasan & Mapping ke Simulink

Tujuan: transform SLD eksisting (3-bus + 3 synchronous gens + loads + lines) menjadi hybrid microgrid per bus.

1) Komponen tambahan per Bus (i = 1..3)

- PV Array block (Simscape)

- MPPT Controller (output: I_ref atau voltage reference ke DC-DC)

- DC–DC Boost (PV → DC-link)

- Battery Pack (Thevenin or detailed cell model) + BMS block

- Bidirectional DC–DC converter (interconnect PV/DC-link/Batt)

- DC link capacitor (stabilize Vdc)

- 3-phase Inverter (VSC) with LC output filter

- AC breaker / contactor between inverter and AC bus

- Local metering: Vabc, Iabc per phase

2) Integrasi ke SLD 3-bus

- Sambungkan output 3-phase of each Inverter ke node Bus i (parallel ke generator sinkron pada bus itu).

- Pastikan urutan prioritas: pada kondisi grid-up, inverter default GRID_FOLLOW, mensinkronkan via PLL. Pada grid-down, EMS mengarahkan salah satu inverter menjadi GRID_FORM.

3) Skema proteksi tambahan

- Per-bus: AC breaker (inverter), DC contactor (batt), anti-islanding relay (per IEEE 1547), directional relays jika ekspor diizinkan.

- Global: master breaker untuk keseluruhan microgrid pada interconnection point (PCC) ke grid.

4) Diagram SLD hybrid (deskripsi tekstual)

- PCC (Point of Common Coupling): titik antar koneksi microgrid dengan external grid (jika ada). Di PCC ada breaker dan relay interkoneksi.

- Bus i sekarang menerima:

  - Generator sinkron (existing)

  - Inverter from PV+Batt

  - Local load

  - Link ke lines antar-bus seperti sebelumnya

Contoh mapping di Simulink:

- Gunakan existing Bus blocks seperti Bus 1, Bus 2, Bus 3.

- Tambahkan per-bus subnetwork PV_BIDIR_INV_Subsystem yang berisi: PV Array -> MPPT -> DC-DC (to DClink) -> DC link -> Bidirectional <-> Battery; DClink -> Inverter 3-phase -> AC breaker -> Bus i.

5) File referensi gambar

- Referensi SLD awal yang Anda kirim: /mnt/data/sld.png (gunakan ini untuk contrast dan overlay di laporan)

D. Bab Skripsi: Arsitektur Kontrol & Implementasi EMS (Draft Siap Pakai)

Judul Bab: Arsitektur Kontrol dan Energi Management System untuk Sistem Hybrid PV–Battery–Inverter pada Jaringan 3-Bus

1. Pendahuluan

Bab ini menjelaskan kerangka kontrol yang dirancang untuk mengoperasikan sistem hybrid berbasis 3-bus. Fokus pada strategi supervisory control untuk memaksimalkan self-consumption, menjaga stabilitas sistem, dan mendukung fitur-fitur seperti TOU scheduling, peak shaving, load shedding, auto-backup (islanding), serta fungsi balancing antar-fase.

2. Tujuan Kontrol

- Menjaga kontinuitas suplai beban kritis di kondisi normal dan gangguan.

- Memaksimalkan penggunaan energi PV (minimalkan import dari grid).

- Menyediakan kemampuan ekspor tenaga ke grid jika menguntungkan.

- Mengoptimalkan penggunaan baterai untuk memperpanjang umur (batery-aware).

- Menjamin keamanan dan proteksi peralatan.

3. Desain Hirarki Kontrol

Level 1 — Local Control (Fast loops)

- MPPT controller: sampling ~ 1–5 kHz, mengeluarkan I/V_ref ke DC–DC.

- Inverter inner current loop: sampling 5–10 kHz, kontrol d/q current PI.

- BMS protections: hardware interlocks, cell balancing.

Level 2 — Supervisory Control (EMS)

- Sampling slower: 100 ms – 1 s. Menangani strategi energi, setpoint, scheduling, dan mode transitions.

Level 3 — Monitoring & SCADA

- Human interface, data logging, remote commanding.

4. Energy Management Strategy

4.1 Prioritas energi

- PV → Supply local critical load

- Excess PV → Charge battery (if SoC < SoC_max)

- If battery full & export allowed → export to grid

- If PV insufficient & SoC > discharge_min → discharge battery

- Else import from grid

4.2 TOU & Economic Dispatch

- EMS maintains tariff calendar, memprediksi biaya & memutuskan charge/discharge untuk mengurangi biaya listrik dan memaksimalkan revenue jika ekspor.

- Untuk penelitian, bandingkan strategi: rule-based vs MPC.

4.3 Battery-aware control

- Include degradation cost in optimizer (cycle count or equivalent life model) to avoid deep-discharge yang tidak perlu.

5. Islanding & Seamless Transfer

5.1 Deteksi kehilangan grid

- Kombinasi: PLL loss, over/under voltage & frequency, detection timers, anti-islanding tests.

5.2 Prosedur islanding

- Isolate PCC breaker

- Pilih master inverter → set to GRID_FORM

- Gradual ramping of voltage & frequency reference

- Activate load shedding if generation < critical demand

5.3 Resynchronization

- Wait until grid back with stable V, f

- Align phase & magnitude, close synchronization breaker under controlled conditions

6. Droop Control and Sharing

- Untuk multiple inverters + synchronous generators, gunakan droop control untuk sharing: P-f and Q-V droops.

- Pilihan parameter droop affects stability & sharing accuracy.

- Implement virtual inertia in inverters (optional) untuk reduce ROCOF and improve damping.

7. Phase Balancing

- Two approaches:

  - Active per-inverter compensation using current controllers adjusting per-phase output

  - Multiple single-phase inverters with EMS allocating P_ref per inverter to balance phases

- EMS periodically evaluates per-phase currents and updates setpoints to minimize negative sequence components.

8. Proteksi dan Interlocking

- Proteksi AC: OC relays, directional relays, anti-islanding per IEEE 1547.

- Proteksi DC: DC fuses, pre-charge resistors, contactors, BMS hard disconnect.

- Fault path & breaker coordination diagrams included di lampiran.

9. Simulasi & Skenario Uji

(List of scenarios from bagian sebelumnya — normal day, peak event, islanding, line fault, battery failure, unbalanced load)

Data yang dihasilkan: energy flows, frequency/voltage traces, SoC trajectories, event logs, KPI per scenario.

10. Implementasi di Simulink

- Struktur folder model: Hybrid_3Bus_main.slx

  - Subsystems: Bus1_Subsystem, Bus2_Subsystem, Bus3_Subsystem, EMS_Controller, Protections, Logger

- Parameter file: params.m yang memuat rating inverter, battery, MPPT params, droop gains, thresholds.

11. Evaluasi & Metodologi Analisis

- Metric ekonomi: operational cost, revenue (if export), net saving vs baseline.

- Metric technical: frequency nadir, voltage deviation, transfer downtime, power sharing errors.

- Statistical analysis across days with stochastic PV and load profiles.

12. Referensi (pilihan awal untuk bab referensi)

- IEEE 1547 — Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces.

- D. Jovcic et al., papers on droop control, virtual inertia.

- MPC for microgrids: academic articles (2016-2024 review papers).

Lampiran: Pseudocode EMS (MATLAB Function-ready)

function [P_ref_inv, Q_ref_inv, I_ref_batt, Mode_inv, Breaker_cmd, Load_shed] = EMS_step(inputs, params)

% inputs struct: P_pv, P_load, SoC, Grid_status, TOU_price, P_gen, Vbus, fbus

% params struct: SoC_max, SoC_min, Export_allowed, Export_limit, Peak_threshold

% Initialize outputs

P_ref_inv = zeros(3,1); Q_ref_inv = zeros(3,1);

I_ref_batt = zeros(3,1); Mode_inv = repmat("GRID_FOLLOW",3,1);

Breaker_cmd = ones(3,1); % 1 = closed

Load_shed = false(3,10); % contoh max 10 loads per bus

for i = 1:3

if ~inputs.Grid_status

% Islanded

Mode_inv(i) = "GRID_FORM"; % selection logic for master omitted

% supply critical loads first

availGen = inputs.P_pv(i) + inputs.P_gen(i) + battery_power_available(inputs.SoC(i));

if availGen >= inputs.P_load(i)

P_ref_inv(i) = inputs.P_load(i);

I_ref_batt(i) = sign(inputs.P_load(i) - inputs.P_pv(i)) * min(batt_max_current, ...);

else

% shed loads until balance

[Load_shed(i,:), P_ref_inv(i), I_ref_batt(i)] = shed_until_balance(...);

end

else

% Grid-connected operations: prioritise PV -> Batt -> Grid

if inputs.P_pv(i) >= inputs.P_load(i)

% surplus

charge_possible = (inputs.SoC(i) < params.SoC_max);

if charge_possible

I_ref_batt(i) = compute_charge_current(inputs.P_pv(i)-inputs.P_load(i));

else

if params.Export_allowed

P_ref_inv(i) = min(inputs.P_pv(i)-inputs.P_load(i), params.Export_limit);

end

end

else

% deficit

if inputs.SoC(i) > params.SoC_discharge_min

I_ref_batt(i) = compute_discharge_current(inputs.P_load(i)-inputs.P_pv(i));

else

% import from grid automatically

P_ref_inv(i) = 0; % inverter idle in grid-follow

end

end

% TOU optimization hook (call optimizer here if available)

end

% protections

if inputs.SoC(i) < params.SoC_cutoff

% disable further discharge

I_ref_batt(i) = 0;

% shed low-priority loads if needed

end

end

end

Penutup

Dokumen ini disusun agar Anda dapat langsung memasukkan blok EMS_Controller, PV_BIDIR_INV_Subsystem ke model Simulink Anda dan memiliki narasi penelitian untuk bab metodologi serta skrip EMS untuk implementasi awal. Jika ingin, saya bisa:

- Menghasilkan file params.m awal dan template Hybrid_3Bus_main.slx dengan struktur folder (perlu tindak lanjut untuk pembuatan file Simulink secara nyata), atau

- Mendesain statechart untuk mode manager (grafik UML/Simulink Stateflow) dan kode Stateflow siap pakai.

Sebutkan pilihan berikutnya Anda.